## Slide 1: Simulations of Heat Transfer to Solid Particles Flowing through a Solar Receiver
2015 NETL Workshop on Multiphase Flow Science
August 12th 2015

## Slide 2: Concentrating Solar Power

## Slide 3: Challenges for CSP technology
How different heat transfer fluids impact design
Operate at high temperatures; T Efficiency
Limit on/off cycling; Day/night and cloud cover
  Thermal storage (Run 24hr/day)

## Slide 4: Challenges for CSP technology
How different heat transfer fluids impact design
Operate at high temperatures; T Efficiency
Limit on/off cycling; Day/night and cloud cover
  Thermal storage (Run 24hr/day)
Candidate Fluids | High Temp? | Thermal Storage?
Steam | Yes | No High pressure overhead
Molten Salts | No they explode | Yes chemical storage

## Slide 5: Challenges for CSP technology
How different heat transfer fluids impact design
Operate at high temperatures; T Efficiency
Limit on/off cycling; Day/night and cloud cover
  Thermal storage (Run 24hr/day)
Candidate Fluids | High T? | Thermal Storage?
Steam | Yes | No High storage costs
Molten Salts | No chemically unstable | Yes
Sand | Yes | Yes

## Slide 6: NREL SunShot CSP Award (PI: Zhiwen Ma)
  Overall Goal: Fundamental, continuum modeling tool that can be used for design of particle receiver: understanding and prediction of heat transfer in solids flows, including radiation
  Why fundamental? Counterintuitive/non-monotonic trends, correlations unreliable for extrapolation
  Why continuum model? Discrete-particle models computationally infeasible

## Slide 7: Model Development for Solar Collector
Overall Approach: Use DEM simulations as “ideal experiment” to test continuum theory
  DEM: instantaneous, local, non-intrusive measurements of concentration, velocity, and temperature
  DEM: can turn various mechanisms on/off to assess relative contributions
Computational Tool: MFIX (Multiphase Flow with Interface eXchanges)
DEM
Continuum

## Slide 8: Heat transfer mechanisms
Conduction
Particle-wall and particle-fluid-wall
Conduction to particles

## Slide 9: Heat transfer mechanisms
Conduction
Particle-wall and particle-fluid-wall
Convection
Entrained gas warmed heated and then heats particles
Conduction to particles
Convective transfer to gas

## Slide 10: Heat transfer to flowing particles
Conductive heat transfer: Particle vs. molecular fluids
Thermal contact “resistance” for particle flows
  Thermal slip for particle flows – molecular fluids often no slip
Twall
Ts,w
Ts,∞
Slip

## Slide 11: Heat transfer to flowing particles
Conductive heat transfer: Particle vs. molecular fluids
Thermal contact “resistance” for particle flows
  Thermal slip for particle flows – molecular fluids often no slip
  Contact resistance depends on how particles contact wall
    Solids concentration near wall
    Particle size / morphology
Twall
Ts,w
Ts,∞
Slip

## Slide 12: Heat transfer to flowing particles
Conductive heat transfer: Particle vs. molecular fluids
Thermal contact “resistance” for particle flows
  Thermal slip for particle flows – molecular fluids often no slip
  Contact resistance depends on how particles contact wall
    Solids concentration near wall
    Particle size / morphology
  Often modeled using Nusselt number correlation
    Existing models are empirical or analytically derived for packed beds
Twall
Ts,w
Ts,∞
Slip

## Slide 13: New continuum heat transfer model
Heat transfer for flowing particles
Account for particle arrangement via “particle-wall” distribution function
  Analogous to radial distribution function
Integrate heat transfer contributions from particles y distance from wall
Measured particle-wall DF from DEM and developed Nu correlation for flowing particles
“classic”
radial distribution function g(r)
new “particle-wall”
distribution function χ(y)
1Morris, A. B., Pannala, S., Ma, Z., and Hrenya, C. M., “A conductive heat transfer model for particle flows over immersed surfaces,” International Journal of Heat and Mass Transfer, vol. 89, 2015, pp. 1277-1289.

## Slide 14: Local Heat Transfer Coefficient: New Model vs. Previous
New model tested for particle flow down top surface of hexagon
  Not tested for full receiver

## Slide 15: DEM Simulations of hexagonal tube array
Base case
~ 6 million particles
Also varied…
Tube spacing
Apex angle
Flow rate
Particle size
Particle Diameter | 300 µm
e (rest. coeff) | 0.9
Solids Mass Flux | 258.2 kg/m2-s
Inlet Temperature | 300 K
Wall Temperature | 600 K
X-spacing | 5.04 cm
Y-spacing | 4.98 cm
Hexagon Width | 3.78 cm
Hexagon Height | 6.42 cm
Apex Angle | 89°

## Slide 16: DEM Simulations of hexagonal tube array
Hydrodynamic instabilities in 2-D vs 3-D
Instabilities develop later in 3-D than 2-D. Still similar to experiments
2-D DEM
Experiments
3-D DEM

## Slide 17: DEM Simulations of hexagonal tube array
Role of Apex Angle
Heat transfer decreases as apex steepens
Apex Angle | Average h [W/m2-K]
89° | 487.41
75° | 371.42
60° | 344.14
Apex = 89°
Apex = 60°

## Slide 18: DEM Simulations of hexagonal tube array
Role of Apex Angle
Heat transfer decreases as apex steepens and as velocity increases
Opposite trend for molecular fluids
Apex Angle | Average h [W/m2-K]
89° | 487.41
75° | 371.42
60° | 344.14
Apex = 89°
Apex = 60°

## Slide 19: DEM Simulations of hexagonal tube array
Role of Particle Size
** Only two rows of hexagons simulated
Slightly stronger instabilities for small particles
Particle size | Average h [W/m2-K]
300 micron | 487.41
200 micron | 780.34
100 micron | 997.23**
Dp = 300µm
Dp = 200µm
~12 million particles

## Slide 20: DEM Simulations of hexagonal tube array
Role of Mass Flow Rate
Less heat transfer at low mass flux (lower concentration)
Mass Flux | Average h [W/m2-K]
258.2 kg/m2-s | 487.41
129.1 kg/m2-s | 313.28
Local heat transfer coefficient
Local heat transfer coefficient

## Slide 21: Comparisons: Local heat transfer coefficient
Particle Diameter
Good agreement for hexagons in 1st and 2nd rows
Lines are continuum model Symbols are DEM
Local heat transfer coefficient
Local heat transfer coefficient

## Slide 22: New continuum model vs DEM
Heat transfer most sensitive to
Particle size
Solids flow rate
Apex angle
New continuum model closely matches DEM

## Slide 23: Conclusions
Conductive heat transfer strongly depends on solids concentration and particle-wall contacts
  Previous models were derived for packed beds and are inaccurate for flowing particles
Heat transfer to flowing particles can be counter-intuitive
  Higher velocity -> less heat transfer
  Increased agitation -> less heat transfer (sometimes)
New model accounts for solids concentration via use of ‘particle-wall’ distribution function
  Accurately matches average heat transfer coefficient (average error less than 5% over all test cases)
  Accurately predicts local heat transfer coefficient
Heat transfer is most sensitive to particle size
  More heat transfer for smaller particles (caveat: no jamming)

## Slide 24: Acknowledgements
Aaron Lattanzi (PhD candidate)
University of Colorado
New!
Ben Grote (Undergraduate researcher)
University of Colorado
New!
This work was funded under the SunShot initiative through the U.S. DOE BRIDGE program (grant no. DE-EE0005954).
The simulations in this work were performed using resources at the Oak Ridge Leadership Computing Facility located at Oak Ridge National Laboratory. This computing facility is supported by the Office of Science of the DOE under contract DE-AC05-00OR22725.
Simulations were also performed on the Janus supercomputer, NSF award number CNS-0821794

## Slide 25: Backup slides

## Slide 26: DEM Simulations of hexagonal tube array
Role of Horizontal Gap Spacing
Δx = {5.04cm, 4.80cm, 4.44cm}
Flow chokes for narrow gap
Δx = 5.04cm
Δx = 4.44cm
Particle Diameter | 300 µm
e (rest. coeff) | 0.9
Solids Mass Flux | 258.2 kg/m2-s
Inlet Temperature | 300 K
Wall Temperature | 600 K

## Slide 27: DEM Simulations of hexagonal tube array
Role of Horizontal Gap Spacing
Heat transfer increases ~20% for narrowest gap
  Flow chokes and improved side wall contact
  Higher surface conc. in top row
x-spacing | Average h [W/m2-K]
5.04 cm | 487.41
4.80 cm | 484.90
4.44 cm | 584.16
Local heat transfer coefficient